## Laut SE-Doku
Common Model MODBUS Register Mappings
Address (base 0) | Address (base 1) | Size | Name | Type | Description | Description2
40000 | 40001 | 2 | C_SunSpec_ID | uint32 | Value = "SunS" (0x53756e53). Uniquely identifies this as a SunSpec MODBUS Map
40002 | 40003 | 1 | C_SunSpec_DID | uint16 | Value = 0x0001. Uniquely identifies this as a SunSpec Common Model Block
40003 | 40004 | 1 | C_SunSpec_Length | uint16 | 65 = Length of block in 16-bit registers
40004 | 40005 | 16 | C_Manufacturer | String(32) | Value Registered with SunSpec = "SolarEdge " | C_Manufacturer is set to SolarEdge.
40020 | 40021 | 16 | C_Model | String(32) | SolarEdge Specific Value | C_Model is set to the appropriate inverter model, e.g. SE5
40044 | 40045 | 8 | C_Version | String(16) | SolarEdge Specific Value | C_Version contains the CPU software version with leading
40052 | 40053 | 16 | C_SerialNumber | String(32) | SolarEdge Unique Value | C_SerialNumber contains the inverter serial number.
40068 | 40069 | 1 | C_DeviceAddress | uint16 | MODBUS Unit ID | C_DeviceAddress is the device MODBUS ID.
Inverter Model MODBUS Register Mappings
Unsupported values are indicated by the NOT_IMPLEMENTED value. The base register of the Device Specific block is set to 40070 (MODBUS PLC address [base 1]), or 40069 (MODBUS Protocol Address [base 0]). - acc32 is a uint32 accumulator that should always increase. Its value is in the range of 0...4294967295. Scale Factors: As an alternative to floating point format, values are represented by Integer values with a signed scale factor applied. The scale factor explicitly shifts the decimal point to left (negative value) or to the right (positive value). For example, a value “Value” may have an associated value “Value_SF” Value = “Value” * 10^ Value_SF for example: • For “Value” = 2071 and “Value_SF” = -2 Value = 2071*10^-2 = 20.71 • For “Value” = 2071 and “Value_SF” = 2 Value = 2071*10^2 = 207100
Address (base 0) | Address (base 1) | Size | Name | Type | Units | Description | Description 2
40069 | 40070 | 1 | C_SunSpec_DID | uint16 |  | 101 = single phase 102 = split phase 103 = three phase
40070 | 40071 | 1 | C_SunSpec_Length | uint16 | Registers | 50 = Length of model block
40071 | 40072 | 1 | I_AC_Current | uint16 | Amps | AC Total Current value
40072 | 40073 | 1 | I_AC_CurrentA | uint16 | Amps | AC Phase A Current value
40073 | 40074 | 1 | I_AC_CurrentB | uint16 | Amps | AC Phase B Current value
40074 | 40075 | 1 | I_AC_CurrentC | uint16 | Amps | AC Phase C Current value
40075 | 40076 | 1 | I_AC_Current_SF | int16 | SF | AC Current scale factor | -2
40076 | 40077 | 1 | I_AC_VoltageAB | uint16 | Volts | AC Voltage Phase AB value
40077 | 40078 | 1 | I_AC_VoltageBC | uint16 | Volts | AC Voltage Phase BC value
40078 | 40079 | 1 | I_AC_VoltageCA | uint16 | Volts | AC Voltage Phase CA value
40079 | 40080 | 1 | I_AC_VoltageAN 1 | uint16 | Volts | AC Voltage Phase A to N value
40080 | 40081 | 1 | I_AC_VoltageBN 1 | uint16 | Volts | AC Voltage Phase B to N value
40081 | 40082 | 1 | I_AC_VoltageCN 1 | uint16 | Volts | AC Voltage Phase C to N value
40082 | 40083 | 1 | I_AC_Voltage_SF | int16 | SF | AC Voltage scale factor
40083 | 40084 | 1 | I_AC_Power | int16 | Watts | AC Power value | Aktuelle Produktion Module/Speicher?
40084 | 40085 | 1 | I_AC_Power_SF | int16 | SF | AC Power scale factor
40085 | 40086 | 1 | I_AC_Frequency | uint16 | Hertz | AC Frequency value
40086 | 40087 | 1 | I_AC_Frequency_SF | int16 | SF | Scale factor
40087 | 40088 | 1 | I_AC_VA | int16 | VA | Apparent Power | Scheinleistung
40088 | 40089 | 1 | I_AC_VA_SF | int16 | SF | Scale factor
40089 | 40090 | 1 | I_AC_VAR | int16 | VAR | Reactive Power | Blindleistung
40090 | 40091 | 1 | I_AC_VAR_SF | int16 | SF | Scale factor
40091 | 40092 | 1 | I_AC_PF | int16 | % | Power Factor
40092 | 40093 | 1 | I_AC_PF_SF | int16 | SF | Scale factor
40093 | 40094 | 2 | I_AC_Energy_WH | acc32 | WattHours | AC Lifetime Energy production
40095 | 40096 | 1 | I_AC_Energy_WH_SF | uint16 | SF | Scale factor
40096 | 40097 | 1 | I_DC_Current | uint16 | Amps | DC Current value |  | Inverter Device Status Values
40097 | 40098 | 1 | I_DC_Current_SF | int16 | SF | Scale factor |  | Parameter | Value | Description
40098 | 40099 | 1 | I_DC_Voltage | uint16 | Volts | DC Voltage value |  | I_STATUS_OFF | 1 | Off
40099 | 40100 | 1 | I_DC_Voltage_SF | int16 | SF | Scale factor |  | I_STATUS_SLEEPING | 2 | Sleeping (auto-shutdown) – Night mode
40100 | 40101 | 1 | I_DC_Power | int16 | Watts | DC Power value |  | I_STATUS_STARTING | 3 | Grid Monitoring/wake-up
40101 | 40102 | 1 | I_DC_Power_SF | int16 | SF | Scale factor |  | I_STATUS_MPPT | 4 | Inverter is ON and producing power
40103 | 40104 | 1 | I_Temp_Sink | int16 | Degrees C | Heat Sink Temperature |  | I_STATUS_THROTTLED | 5 | Production (curtailed)
40106 | 40107 | 1 | I_Temp_SF | int16 | SF | Scale factor |  | I_STATUS_SHUTTING_DOWN | 6 | Shutting down
40107 | 40108 | 1 | I_Status | uint16 |  | Inverter Device Status |  | I_STATUS_FAULT | 7 | Fault
40108 | 40109 | 1 | I_Status_Vendor | uint16 | Error Codes | Vendor-defined operating state and error codes. For error description, meaning and troubleshooting, refer to the SolarEdge Installation Guide. |  | I_STATUS_STANDBY | 8 | Maintenance/setup
Meter # 1 (More Meters? Consult PDF!)
Address (base 0) | Address (base 1) | Size | Name | Type | Units | Description
Common Block
40121 | 40122 | 1 | C_SunSpec_DID | uint16 | N/A | Value = 0x0001. Uniquely identifies this as a SunSpec Common Model Block
40122 | 40123 | 1 | C_SunSpec_Length | uint16 | N/A | 65 = Length of block in 16-bit registers
40123 | 40124 | 16 | C_Manufacturer | String(32) | N/A | Meter manufacturer
40139 | 40140 | 16 | C_Model | String(32) | N/A | Meter model
40155 | 40156 | 8 | C_Option | String(16) | N/A | Export + Import, Production, consumption,
40163 | 40164 | 8 | C_Version | String(16) | N/A | Meter version
40171 | 40172 | 16 | C_SerialNumber | String(32) | N/A | Meter SN
40187 | 40188 | 1 | C_DeviceAddress | uint16 | N/A | Inverter Modbus ID
Identification
40188 | 40189 | 1 | C_SunSpec_DID | uint16 | N/A | Well-known value. Uniquely identifies this as a SunSpecMODBUS Map: Single Phase (AN or AB) Meter (201) Split Single Phase (ABN) Meter (202) Wye-Connect Three Phase (ABCN) Meter (203) Delta-Connect Three Phase (ABC) Meter(204)
40189 | 40190 | 1 | C_SunSpec_Length | uint16 | Registers | Length of meter model block
Current
40190 | 40191 | 1 | M_AC_Current | int16 | Amps | AC Current (sum of active phases)
40191 | 40192 | 1 | M_AC_Current_A | int16 | Amps | Phase A AC Current
40192 | 40193 | 1 | M_AC_Current_B | int16 | Amps | Phase B AC Current
40193 | 40194 | 1 | M_AC_Current_C | int16 | Amps | Phase C AC Current
40194 | 40195 | 1 | M_AC_Current_S F | int16 | SF | AC Current Scale Factor
Voltage
Line to Neutral Voltage
40195 | 40196 | 1 | M_AC_Voltage_L N | int16 | Volts | Line to Neutral AC Voltage (average of active phases)
40196 | 40197 | 1 | M_AC_Voltage_A N | int16 | Volts | Phase A to Neutral AC Voltage
40197 | 40198 | 1 | M_AC_Voltage_B N | int16 | Volts | Phase B to Neutral AC Voltage
40198 | 40199 | 1 | M_AC_Voltage_C N | int16 | Volts | Phase C to Neutral AC Voltage
Line to Line Voltage
40199 | 40200 | 1 | M_AC_Voltage_L L | int16 | Volts | Line to Line AC Voltage (average of active phases)
40200 | 40201 | 1 | M_AC_Voltage_A B | int16 | Volts | Phase A to Phase B AC Voltage
40201 | 40202 | 1 | M_AC_Voltage_B C | int16 | Volts | Phase B to Phase C AC Voltage
40202 | 40203 | 1 | M_AC_Voltage_C A | int16 | Volts | Phase C to Phase A AC Voltage
40203 | 40204 | 1 | M_AC_Voltage_S F | int16 | SF | AC Voltage Scale Factor
Frequency
40204 | 40205 | 1 | M_AC_Freq | int16 | Herts | AC Frequency
40205 | 40206 | 1 | M_AC_Freq_SF | int16 | SF | AC Frequency Scale Factor
Power
Real Power
40206 | 40207 | 1 | M_AC_Power | int16 | Watts | Total Real Power (sum of active phases) | Einspeisung pos, Bezug neg
40207 | 40208 | 1 | M_AC_Power_A | int16 | Watts | Phase A AC Real Power
40208 | 40209 | 1 | M_AC_Power_B | int16 | Watts | Phase B AC Real Power
40209 | 40210 | 1 | M_AC_Power_C | int16 | Watts | Phase C AC Real Power
40210 | 40211 | 1 | M_AC_Power_SF | int16 | SF | AC Real Power Scale Factor
Apparent Power
40211 | 40212 | 1 | M_AC_VA | int16 | Volt- Amps | Total AC Apparent Power (sum of active phases)
40212 | 40213 | 1 | M_AC_VA_A | int16 | Volt- Amps | Phase A AC Apparent Power
40213 | 40214 | 1 | M_AC_VA_B | int16 | Volt- Amps | Phase B AC Apparent Power
40214 | 40215 | 1 | M_AC_VA_C | int16 | Volt- Amps | Phase C AC Apparent Power
40215 | 40216 | 1 | M_AC_VA_SF | int16 | SF | AC Apparent Power Scale Factor
Reactive Power
40216 | 40217 | 1 | M_AC_VAR | int16 | VAR | Total AC Reactive Power (sum of active phases)
40217 | 40218 | 1 | M_AC_VAR_A | int16 | VAR | Phase A AC Reactive Power
40218 | 40219 | 1 | M_AC_VAR_B | int16 | VAR | Phase B AC Reactive Power
40219 | 40220 | 1 | M_AC_VAR_C | int16 | VAR | Phase C AC Reactive Power
40220 | 40221 | 1 | M_AC_VAR_SF | int16 | SF | AC Reactive Power Scale Factor
Power Factor
40221 | 40222 | 1 | M_AC_PF | int16 | % | Average Power Factor (average of active phases)
40222 | 40223 | 1 | M_AC_PF_A | int16 | % | Phase A Power Factor
40223 | 40224 | 1 | M_AC_PF_B | int16 | % | Phase B Power Factor
40224 | 40225 | 1 | M_AC_PF_C | int16 | % | Phase C Power Factor
40225 | 40226 | 1 | M_AC_PF_SF | int16 | SF | AC Power Factor Scale Factor
Accumulated Energy
Real Energy
40226 | 40227 | 2 | M_Exported | uint32 | Watt- hours | Total Exported Real Energy
40228 | 40229 | 2 | M_Exported_A | uint32 | Watt- hours | Phase A Exported Real Energy
40230 | 40231 | 2 | M_Exported_B | uint32 | Watt- hours | Phase B Exported Real Energy
40232 | 40233 | 2 | M_Exported_C | uint32 | Watt- hours | Phase C Exported Real Energy
40234 | 40235 | 2 | M_Imported | uint32 | Watt- hours | Total Imported Real Energy
40236 | 40237 | 2 | M_Imported_A | uint32 | Watt- hours | Phase A Imported Real Energy
40238 | 40239 | 2 | M_Imported_B | uint32 | Watt- hours | Phase B Imported Real Energy
40240 | 40241 | 2 | M_Imported_C | uint32 | Watt- hours | Phase C Imported Real Energy
40242 | 40243 | 1 | M_Energy_W_SF | int16 | SF | Real Energy Scale Factor
Apparent Energy
40243 | 40244 | 2 | M_Exported_VA | uint32 | VA-hours | Total Exported Apparent Energy
40245 | 40246 | 2 | M_Exported_VA_ A | uint32 | VA-hours | Phase A Exported Apparent Energy
40247 | 40248 | 2 | M_Exported_VA_ B | uint32 | VA-hours | Phase B Exported Apparent Energy
40249 | 40250 | 2 | M_Exported_VA_ C | uint32 | VA-hours | Phase C Exported Apparent Energy
40251 | 40252 | 2 | M_Imported_VA | uint32 | VA-hours | Total Imported Apparent Energy
40253 | 40254 | 2 | M_Imported_VA_ A | uint32 | VA-hours | Phase A Imported Apparent Energy
40255 | 40256 | 2 | M_Imported_VA_ B | uint32 | VA-hours | Phase B Imported Apparent Energy
40257 | 40258 | 2 | M_Imported_VA_ C | uint32 | VA-hours | Phase C Imported Apparent Energy
40259 | 40260 | 1 | M_Energy_VA_S F | int16 | SF | Apparent Energy Scale Factor
Reactive Energy
40260 | 40261 | 2 | M_Import_VARh_ Q1 | uint32 | VAR-hours | Quadrant 1: Total Imported Reactive Energy
40262 | 40263 | 2 | M_Import_VARh_ Q1A | uint32 | VAR-hours | Phase A - Quadrant 1: Imported Reactive Energy
40264 | 40265 | 2 | M_Import_VARh_ Q1B | uint32 | VAR-hours | Phase B- Quadrant 1: Imported Reactive Energy |  | Meter Event Values
40266 | 40267 | 2 | M_Import_VARh_ Q1C | uint32 | VAR-hours | Phase C- Quadrant 1: Imported Reactive Energy |  | C_Event Value | Flag | Description
40268 | 40269 | 2 | M_Import_VARh_ Q2 | uint32 | VAR-hours | Quadrant 2: Total Imported Reactive Energy |  | M_EVENT_Power_Failure | 0x00000004 | Loss of power or phase
40270 | 40271 | 2 | M_Import_VARh_ Q2A | uint32 | VAR-hours | Phase A - Quadrant 2: Imported Reactive Energy |  | M_EVENT_Under_Voltage | 0x00000008 | Voltage below threshold (Phase Loss)
40272 | 40273 | 2 | M_Import_VARh_ Q2B | uint32 | VAR-hours | Phase B- Quadrant 2: Imported Reactive Energy |  | M_EVENT_Low_PF | 0x00000010 | Power Factor below threshold (can indicate miss-associated voltage and current inputs in three phase systems)
40274 | 40275 | 2 | M_Import_VARh_ Q2C | uint32 | VAR-hours | Phase C- Quadrant 2: Imported Reactive Energy |  | M_EVENT_Over_Current | 0x00000020 | Current Input over threshold (out of measurement range)
40276 | 40277 | 2 | M_Export_VARh_ Q3 | uint32 | VAR-hours | Quadrant 3: Total Exported Reactive Energy |  | M_EVENT_Over_Voltage | 0x00000040 | Voltage Input over threshold (out of measurement range)
40278 | 40279 | 2 | M_Export_VARh_ Q3A | uint32 | VAR-hours | Phase A - Quadrant 3: Exported Reactive Energy |  | M_EVENT_Missing_Sensor | 0x00000080 | Sensor not connected
40280 | 40281 | 2 | M_Export_VARh_ Q3B | uint32 | VAR-hours | Phase B- Quadrant 3: Exported Reactive Energy |  | M_EVENT_Reserved1 | 0x00000100 | Reserved for future
40282 | 40283 | 2 | M_Export_VARh_ Q3C | uint32 | VAR-hours | Phase C- Quadrant 3: Exported Reactive Energy |  | M_EVENT_Reserved2 | 0x00000200 | Reserved for future
40284 | 40285 | 2 | M_Export_VARh_ Q4 | uint32 | VAR-hours | Quadrant 4: Total Exported Reactive Energy |  | M_EVENT_Reserved3 | 0x00000400 | Reserved for future
40286 | 40287 | 2 | M_Export_VARh_ Q4A | uint32 | VAR-hours | Phase A - Quadrant 4: Exported Reactive Energy |  | M_EVENT_Reserved4 | 0x00000800 | Reserved for future
40288 | 40289 | 2 | M_Export_VARh_ Q4B | uint32 | VAR-hours | Phase B- Quadrant 4: Exported Reactive Energy |  | M_EVENT_Reserved5 | 0x00001000 | Reserved for future
40290 | 40291 | 2 | M_Export_VARh_ Q4C | uint32 | VAR-hours | Phase C- Quadrant 4: Exported Reactive Energy |  | M_EVENT_Reserved6 | 0x00002000 | Reserved for future
40292 | 40293 | 1 | M_Energy_VAR_ SF | int16 | SF | Reactive Energy Scale Factor |  | M_EVENT_Reserved7 | 0x00004000 | Reserved for future
Events | [7 empty] | M_EVENT_Reserved8 | 0x00008000 | Reserved for future
40293 | 40294 | 2 | M_Events | uint32 | Flags | See M_EVENT_ flags. 0 = nts. |  | M_EVENT_OEM1-15 | 0x7FFF000 | Reserved for OEMs

## Alle Register mit Daten
DurchlaufNr | Handle | RegBlock | Reg.00 | Reg.01 | Reg.02 | Reg.03 | Reg.04 | Reg.05 | Reg.06 | Reg.07 | Reg.08 | Reg.09 | Reg.10 | Reg.11 | Reg.12 | Reg.13 | Reg.14 | Reg.15 | Reg.16 | Reg.17 | Reg.18 | Reg.19 | Reg.20 | Reg.21 | Reg.22 | Reg.23 | Reg.24 | Reg.25 | Reg.26 | Reg.27 | Reg.28 | Reg.29 | Reg.30 | Reg.31 | Reg.32 | Reg.33 | Reg.34 | Reg.35 | Reg.36 | Reg.37 | Reg.38 | Reg.39 | Reg.40 | Reg.41 | Reg.42 | Reg.43 | Reg.44 | Reg.45 | Reg.46 | Reg.47 | Reg.48 | Reg.49 | Reg.50 | Reg.51 | Reg.52 | Reg.53 | Reg.54 | Reg.55 | Reg.56 | Reg.57 | Reg.58 | Reg.59 | Reg.60 | Reg.61 | Reg.62 | Reg.63 | Reg.64 | Reg.65 | Reg.66 | Reg.67 | Reg.68 | Reg.69 | Reg.70 | Reg.71 | Reg.72 | Reg.73 | Reg.74 | Reg.75 | Reg.76 | Reg.77 | Reg.78 | Reg.79 | Reg.80 | Reg.81 | Reg.82 | Reg.83 | Reg.84 | Reg.85 | Reg.86 | Reg.87 | Reg.88 | Reg.89 | Reg.90 | Reg.91 | Reg.92 | Reg.93 | Reg.94 | Reg.95 | Reg.96 | Reg.97 | Reg.98 | Reg.99
1 | 1 | 40000 | 21365 | 28243 | 1 | 65 | 21359 | 27745 | 29253 | 25703 | 25888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21317 | 12592 | 19245 | 21079 | 21300 | 14402 | 17742 | 13312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12336 | 12340 | 11824 | 12337 | 13358 | 12338 | 12856 | 0 | 14149 | 12342 | 12599 | 17204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 103 | 50 | 246 | 82 | 80 | 83 | -2 | 3998 | 4005 | 4010 | 2306 | 2318 | 2312 | -1 | 3780 | -1 | 4994 | -2 | 5680 | -1 | -4240 | -1 | -6644 | -2 | 33 | 27423 | 0 | 4690 | -4 | 8180 | -1 | 0
1 | 2 | 40100 | 3837 | -1 | -32768 | 4189 | -32768 | -32768 | -2 | 4 | 0 | -1 | -1 | -1 | -1 | 0 | 0 | -1 | -1 | -1 | -1 | 0 | 0 | 1 | 65 | 21359 | 27745 | 29253 | 25703 | 25856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21317 | 11597 | 21586 | 11571 | 22829 | 13360 | 12374 | 11585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17784 | 28783 | 29300 | 11081 | 28016 | 28530 | 29696 | 0 | 12592 | 14135 | 0 | 0 | 0 | 0 | 0 | 0 | 13872 | 13879 | 13623 | 13365 | 13056 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 203 | 105 | 43 | 19 | 14 | 9 | -1 | 23051 | 23051 | 23127 | 23096 | 0 | 0
1 | 3 | 40200 | 0 | 0 | 0 | -2 | 4995 | -2 | -20 | -142 | 8 | 113 | 0 | 852 | 376 | 304 | 228 | 0 | -851 | -348 | -304 | -198 | 0 | -800 | 2919 | -329 | -4990 | -2 | 19 | 14845 | 5 | 7004 | 8 | 20428 | 9 | -29678 | 4 | -12296 | 5 | 24180 | 1 | -15140 | 1 | 27109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -32768 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -32768 | 0 | 0 | 701 | 153 | 2 | 1 | -1 | 0
1 | 4 | 40300 | 1 | 0 | 0 | -1 | -1 | 10000 | 10009 | 431 | 66 | -32768 | 3995 | 2306 | 0 | -15589 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -32768 | -32768 | -32768 | -32768 | -32768 | -32768 | -32768 | -32768 | -32768 | -1 | -1 | -1 | 2306 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -32768 | -32768 | -32768 | -1 | -1 | -1 | 2316 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -32768 | -32768 | -32768 | -1 | -1 | -1 | 2310 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0
1 | 5 | 40400 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | -1 | -3 | 0 | -2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 702 | 50 | 10000 | 8000 | 80 | 8000 | 80 | 10000 | 6000 | 6000 | -1 | -1 | -1 | -1 | 2300 | 2530 | 2023 | -1 | -1 | -1 | 0 | 1 | 2 | -1 | -2049 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | -2 | 0 | 0 | -1 | 0
1 | 6 | 40500 | 0 | 0 | 703 | 17 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -2 | -3 | 704 | 65 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | -1 | -1 | -32768 | 0 | -32768 | -32768 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | -1 | -1 | -1 | -32768 | 0 | -1 | -32768 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -3 | -2 | 0 | -2 | 0 | -2 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 705 | 57 | 0 | 0 | 1 | 6 | 2 | -1 | -1 | -1 | -1 | -1 | 0
1 | 7 | 40600 | -2 | -2 | -3 | 6 | 0 | 0 | 100 | 0 | 0 | 441 | 0 | 11665 | 1 | 5000 | 4359 | 9300 | 4359 | 9700 | 0 | 10300 | 0 | 10700 | -4359 | 11999 | -4359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 706 | 47 | 0 | 0 | 1 | 6 | 2 | -1 | -1 | -1 | -1 | -1 | -2 | 0 | -3 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 707 | 105 | -1 | 0 | 0
1 | 8 | 40900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 709 | 135 | 1 | 0 | 1 | 5 | 2 | -2 | -3 | 0 | 1 | 0 | 4750 | 0 | 100 | 0 | 2000 | 8 | -9824 | 0 | 2000 | 8 | -9824 | 0 | 2000 | 8 | -9824 | 0 | 2000 | 8 | -9824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | 41000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 710 | 135 | 1 | 0 | 1 | 5 | 2 | -2 | -3 | 0 | 5 | 0 | 5150 | 0 | 100 | 0 | 10000 | 8 | -9824 | 0 | 10000 | 8 | -9824 | 0 | 10000 | 8 | -9824 | 0 | 10000 | 8 | -9824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 10 | 41100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 711 | 32 | -1 | 0 | 0 | 2 | -1 | -1 | -1 | -1 | -1 | -3 | -3 | -3 | 0 | 0 | 0
1 | 11 | 56600 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 100 | 0 | 0 | 0 | 100 | 17096 | 0 | 0 | 200 | 17096 | 0 | 0 | 200 | 17096 | 0 | 0 | 200 | 17096 | 0 | 0 | 200 | 17096 | 0 | 0 | 200 | 16928 | 0 | 0 | 100 | 16928 | 0 | 0 | 100 | 16928 | 0 | 0 | 100 | 16928 | 0 | 0 | 100 | 16928 | 0 | 0 | 100 | 17416 | -3915 | 0 | 2000 | 17455 | 0 | 0 | 200 | 17455 | 0 | 0 | 200 | 17455 | 0 | 0 | 200 | 17455 | 0 | 0 | 200 | 17455 | 0 | 0 | 200 | 17455 | 0 | 0 | 200 | 17455 | 0 | 0 | 200 | 17455 | 0 | 0 | 200 | 17455 | 0 | 0 | 200 | 17185 | 22316 | 0 | 2000 | 0
1 | 12 | 59400 | 0 | 0 | 0 | 0 | 3600 | -1 | 17820 | 16384 | 17820 | 16384 | 0 | 0 | 3 | -129 | -1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 15 | 17945 | -7168 | -1 | -1 | -1 | 67 | -22253 | -16744 | 6916 | 37 | 2048 | 0 | 18304 | 36 | -22253 | -16744 | 1 | 0 | -22248 | -16744 | -9817 | 12 | -21664 | -16744 | 16986 | 40 | -6136 | 0 | 7839 | 22 | -22253 | -16744 | 19273 | 0 | -22212 | -16744 | 21 | 0 | 597 | 0 | 597 | 0 | 0 | 0 | 100 | 0 | -29696 | 588 | 4 | 0 | 0 | 0 | 0 | 0 | 3600 | -1 | 17820 | 16384 | 17820 | 16384 | 0 | 0 | 3 | -129 | -1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
1 | 13 | 61700 | 2 | 0 | 200 | 0 | 1 | 0 | 0 | 16256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16968 | 0 | 17096 | 0 | 17096 | 0 | 17096 | 0 | 16256 | 0 | 16256 | 0 | 16256 | 26215 | -16538 | 26215 | -16538 | 26215 | -16538 | 0 | 16968 | 0 | 17082 | 0 | 17090 | 0 | 17102 | 1 | 17110 | -1 | 17135 | 26213 | -15826 | 26213 | -15826 | 0 | 0 | 0 | 0 | 26213 | 16942 | 26213 | 16942 | 0 | 16384 | 0 | 17096 | 1 | 0 | 2 | 0 | 26214 | 16968 | 0 | 16958 | 0 | 17277 | -32768 | 17219 | 0 | 17254 | -7599 | 16743 | -13107 | 16968 | -13107 | 16976 | 0 | 17096 | 0 | 16800 | -13107 | 16968 | 0 | 16976 | 0 | 0 | 0 | 16968 | -1 | 17007 | -1 | 17055 | 0 | 17076 | 0
1 | 14 | 61800 | 0 | 17096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 30176 | 9 | 30176 | 9 | 0 | 0 | 0 | 16384 | 0 | 0 | 0 | 16384 | 0 | 0 | 0 | 16384 | 0 | 0 | 0 | 16384 | 0 | 0 | 10176 | 9 | 22624 | 17129 | -1 | 16671 | 0 | 17096 | 1 | 17110 | 0 | 17116 | 0 | 17126 | 0 | 17146 | 0 | 17096 | 0 | 17096 | 0 | 17096 | 0 | 17096 | 0 | 17096 | 0 | 17096 | 1 | 0 | 3333 | 0 | 0 | 17066 | 3333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 15 | 63800 | 0 | 0 | 16942 | 26213 | 16942 | 26213 | 16384 | 0 | 17096 | 0 | 0 | 1 | 0 | 2 | 16968 | 26214 | 16958 | 0 | 17277 | 0 | 17219 | -32768 | 17254 | 0 | 16743 | -7599 | 16968 | -13107 | 16976 | -13107 | 17096 | 0 | 16800 | 0 | 16968 | -13107 | 16976 | 0 | 0 | 0 | 16968 | 0 | 17007 | -1 | 17055 | -1 | 17076 | 0 | 17096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 30176 | 9 | 30176 | 0 | 0 | 16384 | 0 | 0 | 0 | 16384 | 0 | 0 | 0 | 16384 | 0 | 0 | 0 | 16384 | 0 | 0 | 0 | 9 | 10176 | 17129 | 22624 | 16671 | -1 | 17096 | 0 | 17110 | 1 | 17116 | 0 | 17126 | 0 | 17146 | 0 | 0
1 | 16 | 64800 | 14388 | 8278 | 17220 | 17220 | 12832 | 12846 | 14638 | 8241 | 19778 | 8275 | 11824 | 11824 | 48 | 0 | 0 | 0 | 17719 | 13872 | 14129 | 13379 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112 | 0 | 17996 | -20480 | 17820 | 16384 | 17820 | 16384 | 17820 | 16384 | 17820 | 16384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16815 | 13107 | 0 | 0 | 17484 | -1269 | 16160 | 9296 | -15392 | -32768 | 0 | 0 | 0 | 313 | 0 | 0 | 0 | 0 | 17996 | -20480 | 17985 | -16384 | 17096 | 0 | 0
1 | 17 | 65300 | 3 | -129 | -1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 15 | 17945 | -7168 | -1 | -1 | -1 | 0 | -22253 | -16744 | 6916 | 37 | 2048 | 0 | 18304 | 36 | -22253 | -16744 | 1 | 0 | -22248 | -16744 | -9817 | 12 | -21664 | -16744 | 16986 | 40 | -236 | 0 | 7839 | 22 | -22253 | -16744 | 0 | 0 | 0 | 0 | 0 | 0 | 602 | 0 | 602 | 0 | 0 | 0 | 100 | 0 | 0 | 512 | 4 | 0 | 3 | -129 | -1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 15 | 17945 | -7168 | -1 | -1 | -1 | 0 | -22253 | -16744 | 6916 | 37 | 2048 | 0 | 18304 | 36 | -22253 | -16744 | 1 | 0 | -22248 | -16744 | -9817 | 12 | 0